## Concentrations
Interim Water Treatment Plant Inlet and Outlet Concentrations
(Concentrations in micrograms per liter)
| 2015-10-19 |  | 10/22/2015 481 GPM |  | 10/26/2015 422 GPM |  | 10/29/2015 404 GPM |  | 11/3/2015 557 GPM |  | 11/5/2015 570 GPM |  | 12/1/2015* 526 GPM |  | 12/8/2015 514 GPM |  | 12/17/2015 571 GPM |  | 12/23/2015 521 GPM |  | 1/5/2016 487 GPM |  | 2/3/2016 614 GPM |  | 2/4/2016 671 GPM |  | 2/5/2016 676 GPM |  | 2/18/2016 508 GPM |  | 3/25/2016 514 GPM |  | 4/12/2016 638 GPM |  | 4/12/2016 746 GPM |  | 4/12/2016 961 GPM
| In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out
Aluminum | 20000 | 4100 | 20000 | 1300 | 20000 | 4200 | 21000 | 6500 | 21000 | 12000 | 21000 | 12000 | NS | 9400 | 17000 | 5100 | 17000 | 4800 | 18000 | 5000 | NS | 6300 | NS | 3200 | 15000 | 330 | NS | 320 | 14000 | 820 | 14000 | 200 | 13000 | 190 J | 13000 | 170 J | 13000 | 170 J
Aluminum, Dissolved | 19000 | 1700 | 19000 | 570 J- | 19000 | 480 | 20000 | 1500 | 19000 | 230 | 19000 | 420 | NS | 2800 J | 12000 | NA | 12000 | 197 | 12000 | 370 | NS | 210 | NS | 1100 | 8000 | 200 | NS | 190 J | 12000 | 96 J | 5100 | 92 J | 4700 | 100 J | 4700 |  | 4700 | 110 J
Antimony | 2.3 | 0.4 U | 2.5 | 0.4 U | 2.3 | 0.4 U | 2.4 | 0.4 U | 2.3 | 1 | 2.3 | 0.83 J | NS | 0.6 J | 1.9 | 0.7 | 1.9 | 0.8 | 1.9 | 0.8 | NS | 0.8 J | NS | 0.45 J | 1.8 | 0.4 U | NS | 0.4 U | 1.8 | 0.4 U | 1.6 | 0.4 U | 1.4 | 0.4 U | 1.4 | 0.4 U | 1.4 | 0.4 U
Antimony, Dissolved | 0.4 U | 0.4 U | 0.4 U | 0.4 UJ | 0.48 J | 0.55 J | 1.9 | 0.4 U | 0.42 J | 0.4 U | 0.4 U | 0.4 U | NS | 0.4 U | 0.4 U | NA | 0.4 U | 0.4 U | 0.4 U | 0.4 J | NS | 0.4 J | NS | 0.4 U | 0.4 U | 0.4 U | NS | 0.4 U | 1.3 | 0.4 U | 0.48 J | 0.57 J | 0.42 J | 0.4 U | 0.42 J |  | 0.42 J | 0.4 U
Arsenic | 26 | 0.93 J | 29 | 0.37 U | 27 | 2.3 | 30 | 4.2 | 28 | 11 | 29 | 8.7 | NS | 6.1 | 24 | 5 | 23 | 6 | 23 | 6.9 | NS | 5.9 | NS | 4 | 23 | 0.37 U | NS | 0.37 U | 21 | 1 | 20 | 0.37 U | 17 | 0.37 U | 17 | 0.37 U | 17 | 0.37 U
Arsenic, Dissolved | 1.1 | 0.37 U | 2.1 | 0.37 UJ | 2.6 | 0.37 U | 23 | 0.37 U | 1.5 | 0.37 U | 1.6 | 0.37 U | NS | 0.37 U | 1.3 | NA | 1.3 | 0.37 U | 1.3 | 0.49 | NS | 0.38 U | NS | 1.3 | 1.6 | 0.37 U | NS | 0.37 U | 13 | 0.37 U | 0.86 J | 0.37 U | 1.5 | 0.37 U | 1.5 |  | 1.5 | 0.37 U
Barium | 9.5 | 8.5 | 9.6 | 7.8 | 9.2 | 8.7 | 9.8 | 9.7 | 9.5 | 11 | 9.6 | 9.8 | NS | 9.9 | 9.7 | 8.6 | 9.5 | 9.2 | 9 | 8.6 | NS | 9.1 | NS | 8.9 | 10 | 8.4 | NS | 8.2 | 10 | 8.1 | 10 | 8.3 | 9.6 | 8.4 | 9.6 | 8.4 | 9.6 | 8.5
Barium, Dissolved | 9.3 | 8.8 | 9.6 | 8.8 J- | 9.3 | 8.2 | 9.8 | 8.1 | 9.6 | 8.3 | 9.7 | 7.9 | NS | 9.2 | 160 | NA | 41 | 48 | 9.1 | 9.5 | NS | 8.2 | NS | 9.1 | 10 | 8.6 | NS | 8.3 | 35 | 39 | 9.5 | 25 | 9.3 | 8.2 | 9.3 |  | 9.3 | 8.7
Beryllium | 8 | 1.3 | 9.4 | 0.36 J | 9.3 | 1.7 | 9.8 | 2.4 | 8 | 4.6 | 7.3 | 4.2 | NS | 4.2 | 7.1 | 1.97 | 6.9 | 2.1 | 6.9 | 2.2 | NS | 2.8 | NS | 1.3 | 6.9 | 0.15 U | NS | 0.15 U | 5.8 | 0.27 J | 5.5 | 0.15 U | 5 | 0.15 U | 5 | 0.15 U | 5 | 0.15 U
Beryllium, Dissolved | 8.1 | 0.32 J | 8.7 | 0.15 UJ | 9 | 0.15 U | 9.3 | 0.15 U | 7 | 0.15 U | 6.9 | 0.15 U | NS | 1.8 | 5.7 | NA | 5.6 | 0.15 U | 5.8 | 0.2 | NS | 0.15 U | NS | 0.49 | 4.2 | 0.15 U | NS | 0.15 U | 4.6 | 0.15 U | 2.9 | 0.15 U | 2.5 | 0.15 U | 2.5 |  | 2.5 | 0.15 U
Cadmium | 53 | 10 | 44 | 4.2 | 52 | 13 | 57 | 15 | 55 | 33 | 56 | 34 | NS | 53 | 46 | 16 | 45 | 19 | 46 | 16 | NS | 20 | NS | 16 | 46 | 4.2 | NS | 4.2 | 36 | 4.4 | 40 | 4.5 | 36 | 5.8 | 36 | 4.6 | 36 | 4.4
Cadmium, Dissolved | 57 | 3.3 | 44 | 2.8 J- | 57 | 2.8 | 56 | 0.17 J | 58 | 6.3 | 57 | 2.5 | NS | 44 | 47 | NA | 47 | 4.4 | 49 | 4.4 | NS | 4.5 | NS | 10 | 46 | 3.6 | NS | 3.8 | 35 | 3.1 | 39 | 4.1 | 37 | 5.4 | 37 |  | 37 | 4.1
Calcium | 340000 | 470000 | 350000 | 470000 | 350000 | 480000 | 380000 | 550000 | 400000 | 510000 | 380000 | 510000 | NS | 440000 | 350000 | 450000 | 350000 | 440000 | 370000 | 460000 | NS | 460000 | NS | 450000 | 370000 | 450000 | NS | 460000 | 360000 | 450000 | 370000 | 430000 | 360000 | 420000 | 360000 | 420000 | 360000 | 420000
Calcium, Dissolved | 340000 | 470000 | 350000 | 480000 | 360000 | 480000 | 370000 | 530000 | 390000 | 520000 | 380000 | 510000 | NS | 430000 | 340000 | NA | 350000 | 430000 | 360000 | 420000 | NS | 470000 | NS | 440000 | 370000 | 440000 | NS | 440000 | 370000 | 450000 | 370000 | 430000 | 360000 | 420000 | 360000 |  | 360000 | 410000
Chromium | 2.5 | 1 U | 2.9 | 1 U | 2.8 | 1 U | 2.8 | 1.2 J | 2.9 | 1.9 J | 2.9 | 1.8 J | NS | 1.5 J | 2.6 | 1.7 | 2.5 | 1.8 | 2.2 | 1.8 | NS | 1.9 | NS | 1 U | 2.4 | 1 U | NS | 1 U | 2.1 | 1 U | 2 | 1 U | 1.8 J | 1 U | 1.8 J | 1 U | 1.8 J | 1 U
Chromium, Dissolved | 1 U | 1 U | 1 U | 1 UJ | 1 U | 1 U | 2.2 | 1 U | 1 U | 1 U | 1 U | 1 U | NS | 1 U | 1 U | NA | 1 U | 1 U | 1 U | 1 U | NS | 1 U | NS | 1 U | 1 U | 1 U | NS | 1 U | 1.2 J | 1 U | 1 U | 1 U | 1 U | 1 U | 1 U |  | 1 U | 1 U
Cobalt | 79 | 15 | 82 | 8.7 | 76 | 21 | 86 | 23 | 80 | 51 | 82 | 49 | NS | 74 | 72 | 21 | 70 | 27 | 67 | 27 | NS | 33 | NS | 27 | 63 | 9.9 | NS | 10 | 61 | 10 | 60 | 12 | 54 | 14 | 54 | 11 | 54 | 11
Cobalt, Dissolved | 79 | 5.1 | 82 | 6.5 J- | 80 | 5.7 | 81 | 0.89 | 81 | 12 | 80 | 3.5 | NS | 58 | 69 | NA | 70 | 11 | 67 | 10 | NS | 11 | NS | 20 | 61 | 9.3 | NS | 9.4 | 59 | 8 | 58 | 12 | 53 | 13 | 53 |  | 53 | 11
Copper | 4500 | 720 | 4600 | 170 | 4300 | 840 | 4800 | 1200 | 4400 | 2600 | 4500 | 2500 | NS | 2100 | 3700 | 1300 | 3700 | 1300 | 3600 | 1100 | NS | 1500 | NS | 730 | 3500 | 29 | NS | 30 | 3300 | 140 | 3200 | 26 | 2900 | 25 | 2900 | 20 | 2900 | 22
Copper, Dissolved | 4400 | 170 | 4500 | 13 J- | 4600 | 1.6 | 4800 | 3.7 | 4300 | 25 | 4300 | 1.4 | NS | 680 | 3500 | NA | 3500 | 5.5 | 3400 | 40 | NS | 9.2 | NS | 250 | 3000 | 4.2 | NS | 5.4 | 3000 | 1.7 | 2500 | 1.7 | 2100 | 1.5 | 2100 |  | 2100 | 2.2
Iron | 86000 | 10000 | 85000 | 2700 | 84000 | 13000 | 85000 | 18000 | 85000 | 42000 | 85000 | 40000 | NS | 50000 | 73000 | 18000 | 71000 | 18800 | 74000 | 19000 | NS | 24000 | NS | 14000 | 66000 | 520 | NS | 540 | 60000 | 2500 | 57000 | 400 | 52000 | 410 | 52000 | 300 | 52000 | 340
Iron, Dissolved | 59000 | 2300 | 60000 | 170 J- | 60000 | 42 J | 77000 | 33 J | 59000 | 420 J | 58000 | 29 J | NS | 26000 | 52000 | NA | 52000 | 31 | 52000 | 615 | NS | 32 | NS | 4400 | 46000 | 72 | NS | 71 | 56000 | 17 U | 37000 | 17 U | 36000 | 17 U | 36000 |  | 36000 | 25 J
Lead | 32 | 3.5 | 32 | 0.8 | 29 | 3.7 | 30 | 6.1 | 29 | 19 | 30 | 11 | NS | 6.6 | 26 | 5 | 26 | 6.3 | 26 | 7.4 | NS | 6.8 | NS | 4.6 | 26 | 0.24 J | NS | 0.17 J | 25 | 1.7 | 22 | 0.15 J | 19 | 0.17 J | 19 | 0.06 U | 19 | 0.06 U
Lead, Dissolved | 14 | 1.2 | 15 | 0.24 J- | 15 | 0.06 U | 27 | 0.067 J | 9.6 | 0.16 J | 7.3 | 0.06 U | NS | 0.3 | 2.9 | NA | 2.6 | 0.06 U | 2.9 | 0.26 | NS | 0.06 U | NS | 1.5 | 1.5 | 0.06 U | NS | 0.078 J | 18 | 0.2 J | 0.77 | 0.06 U | 0.89 | 0.073 J | 0.89 |  | 0.89 | 0.2 J
Magnesium | 19000 | 18000 | 20000 | 17000 | 20000 | 18000 | 23000 | 5500 | 22000 | 21000 | 21000 | 19000 | NS | 20000 | 19000 | 17000 | 19000 | 18000 | 19000 | 17000 | NS | 18000 | NS | 17000 | 18000 | 17000 | NS | 17000 | 17000 | 16000 | 17000 | 15000 | 16000 | 14000 | 16000 | 14000 | 16000 | 15000
Magnesium, Dissolved | 19000 | 18000 | 20000 | 18000 | 21000 | 18000 | 22000 | 230 J | 22000 | 19000 | 20000 | 18000 | NS | 19000 | 19000 | NA | 19000 | 17000 | 19000 | 16000 | NS | 17000 | NS | 17000 | 18000 | 16000 | NS | 16000 | 18000 | 16000 | 17000 | 16000 | 16000 | 14000 | 16000 |  | 16000 | 14000
Manganese | 28000 | 12000 | 28000 | 11000 | 27000 | 16000 | 29000 | 7500 | 29000 | 26000 | 30000 | 23000 | NS | 28000 | 26000 | 13000 | 26000 | 19000 | 24000 | 18000 | NS | 19000 | NS | 19000 | 24000 | 15000 | NS | 15000 | 22000 | 14000 | 23000 E | 16000 E | 20000 E | 14000 E | 20000 E | 14000 E | 20000 E | 13000 E
Manganese, Dissolved | 28000 | 9900 | 29000 | 12000 | 28000 | 13000 | 29000 | 18 | 30000 | 20000 | 29000 | 13000 | NS | 25000 | 25000 | NA | 25000 | 17000 | 24000 | 14000 | NS | 15000 | NS | 19000 | 23000 | 15000 | NS | 14000 | 21000 | 13000 | 22000 E | 16000 E | 20000 E | 14000 E | 20000 E |  | 20000 E | 13000 E
Mercury | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | NS | 0.1 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | NS | 0.08 U | NS | NA | NA | NA | NS | NA | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U
Mercury, Dissolved | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | NS | 0.1 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | NS | 0.08 U | NS | NA | NA | NA | NS | NA | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U | 0.08 U |  | 0.08 U | 0.08 U
Molybdenum | 3.3 | 0.45 U | 3.8 | 0.59 J | 3.7 | 0.9 J | 3.9 | 1.5 | 3.8 | 2.3 | 3.8 | 1.8 | NS | 1.4 | 3.6 | 1.8 | 3.4 | 2 | 3.4 | 2.1 | NS | 1.9 | NS | 1.8 | 3.4 | 1.7 | NS | 1.7 | 3.2 | 2.4 | 3.1 | 1.8 | 3 | 1.4 | 3 | 1.2 | 3 | 1.2
Molybdenum, Dissolved | 0.45 U | 0.45 U | 0.45 U | 0.7 J- | 0.69 J | 0.8 J | 3.1 | 1.1 | 0.45 U | 1.4 | 0.45 U | 0.96 J | NS | 0.7 J | 0.64 J | NA | 0.55 J | 1.7 | 0.7J | 1.6 | NS | 1.5 | NS | 1.7 | 0.45 U | 1.7 | NS | 1.7 | 2.2 | 2.3 | 0.46 | 1.7 | 0.72 J | 1.3 | 0.72 J |  | 0.72 J | 1
Nickel | 45 | 11 | 47 | 7.8 | 43 | 14 | 49 | 17 | 46 | 32 | 48 | 32 | NS | 41 | 44 | 20 | 43 | 24 | 46 | 28 | NS | 31 | NS | 17 | 37 | 8.3 | NS | 8.5 | 38 | 10 | 37 | 13 | 36 | 16 | 36 | 14 | 36 | 14
Nickel, Dissolved | 47 | 5.9 | 48 | 8.4 J- | 46 | 6.5 | 48 | 5.1 | 47 | 11 | 47 | 6.2 | NS | 33 | 44 | NA | 43 | 15 | 45 | 18 | NS | 19 | NS | 14 | 36 | 8.3 | NS | 8.4 | 37 | 9.1 | 37 | 13 | 36 | 16 | 36 |  | 36 | 14
Potassium | 2200 | 2300 | 2200 J+ | 2300 J+ | 2300 | 2400 | 2500 J+ | 2600 J+ | 2300 | 2500 | 2300 | 2400 | NS | 2300 | 1900 | 2000 | 1900 | 2000 | 2100 | 2100 | NS | 2120 | NS | 2700 J+ | 2300 J+ | 2800 J+ | NS | 2800 J+ | 2100 | 2300 | 1900 | 2000 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
Potassium, Dissolved | 2300 | 2400 | 2300 | 2400 J | 2300 J+ | 2400 | 2500 J+ | 2700 J+ | 2300 J+ | 2400 | 2200 J+ | 2300 | NS | 2300 | 1800 | NA | 1900 | 1800 | 2000 J+ | 2000 | NS | 2130 | NS | 2800 J+ | 2500 J+ | 2800 J+ | NS | 2700 J+ | 2100 | 1900 | 1900 | 1900 | 1800 | 1800 | 1800 |  | 1800 | 1800
Selenium | 0.91 J | 0.58 U | 1.8 J | 0.58 U | 1.8 J | 0.58 U | 1.8 J | 0.58 U | 1.6 J | 0.73 J | 1.7 J | 0.58 U | NS | 1.0 J | 1.4 J | 1 | 1.4 J | 0.95 J | 2.1 | 1.1 | NS | 1.3 | NS | 0.58 U | 1.7 J | 0.58 U | NS | 0.58 U | 1.5 J | 0.58 U | 0.83 J | 0.58 U | 0.61 J | 0.58 U | 0.61 J | 0.58 U | 0.61 J | 0.58 U
Selenium, Dissolved | 0.81 J | 0.58 U | 1.3 J | 0.58 UJ | 1.3 J | 0.58 U | 1.2 J | 0.58 U | 1.3 J | 0.58 U | 1.4 J | 0.58 U | NS | 0.7 U | 1.2 J | NA | 0.95 J | 0.58 U | 1.8 J | 0.58 U | NS | 0.59 U | NS | 0.58 U | 1.1 J | 0.58 U | NS | 0.58 U | 1.1 J | 0.58 U | 0.58 U | 0.58 U | 0.58 U | 0.58 U | 0.58 U |  | 0.58 U | 0.58 U
Silver | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | NS | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.11 J | NS | 0.11 U | NS | 0.1 U | 0.1 U | 0.1 U | NS | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U
Silver, Dissolved | 0.1 U | 0.1 U | 0.1 U | 0.1 UJ | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | NS | 0.1 U | 0.1 U | NA | 0.1 U | 0.1 U | 0.1 U | 0.10 U | NS | 0.10 U | NS | 0.1 U | 0.1 U | 0.1 U | NS | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U | 0.1 U |  | 0.1 U | 0.1 U
Sodium | 7300 | 7100 | 5000 | 7400 | 2200 | 5200 | 1700 | 5100 | 1300 | 3800 | 1400 | 3100 | NS | 2600 | 2100 J+ | 5600 | 2100 J+ | 5300 | 2900 | 5600 | NS | 5530 | NS | 4700 | 3600 | 5500 | NS | 5500 | 3400 | 5400 | 2900 | 4900 | 2600 | 4600 | 2600 | 4700 | 2600 | 4600
Sodium, Dissolved | 7700 | 7500 | 5200 | 7900 J- | 2300 | 5800 | 1800 | 6200 | 1500 | 5600 | 2600 | 5700 | NS | 2900 | 4600 | NA | 2500 | 5600 | 2900 | 5200 | NS | 5770 | NS | 5400 J+ | 3800 J+ | 5600 J+ | NS | 5400 J+ | 4000 | 6100 | 2800 | 5200 | 2500 | 4700 | 2500 |  | 2500 | 4600
Thallium | 0.22 | 0.17 J | 0.23 | 0.16 J | 0.2 | 0.17 J | 0.25 | 0.15 J | 0.22 | 0.2 | 0.21 | 0.19 J | NS | 0.2 | 0.21 | 0.16 | 0.19 J | 0.17 J | 0.18 J | 0.15 J | NS | 0.15 | NS | 0.15 J | 0.17 J | 0.12 J | NS | 0.12 J | 0.18 J | 0.12 J | 0.17 J | 0.14 J | 0.15 J | 0.12 J | 0.15 J | 0.13 J | 0.15 J | 0.13 J
Thallium, Dissolved | 0.21 | 0.17 J | 0.23 | 0.2 J- | 0.22 | 0.16 J | 0.24 | 0.11 J | 0.21 | 0.18 J | 0.2 | 0.14 J | NS | 0.2 J | 0.1 | NA | 0.1 U | 0.1 U | 0.18 J | 0.13 J | NS | 0.14 | NS | 0.13 J | 0.15 J | 0.12 J | NS | 0.12 J | 0.11 J | 0.1 U | 0.15 J | 0.12 J | 0.14 J | 0.12 J | 0.14 J |  | 0.14 J | 0.12 J
Vanadium | 21 | 0.83 J | 21 | 0.46 J | 20 | 1.8 | 21 | 3.7 | 21 | 9.6 | 21 | 8.2 | NS | 5.3 | 18 | 4.8 | 18 | 5.3 | 17 | 5.1 | NS | 5.6 | NS | 3.5 | 16 | 0.3 U | NS | 0.3 U | 16 | 1 | 15 | 0.3 U | 13 | 0.3 U | 13 | 0.3 U | 13 | 0.3 U
Vanadium, Dissolved | 0.3 U | 0.3 U | 0.51 J | 0.3 UJ | 0.92 J | 0.3 U | 16 | 0.3 U | 0.3 U | 1 UB | 0.3 U | 0.3 U | NS | 0.3 U | 0.3 U | NA | 0.3 U | 0.3 U | 0.3 U | 0.4 | NS | 0.3 U | NS | 1.2 | 0.3 U | 0.3 U | NS | 0.3 U | 9.8 | 0.3 U | 0.3 U | 0.3 U | 0.3 U | 0.3 U | 0.3 U |  | 0.3 U | 0.3 U
Zinc | 18000 | 2900 | 19000 | 750 | 17000 | 3500 | 20000 | 4700 | 18000 | 9900 | 18000 | 10000 | NS | 15000 | 15000 | 5100 | 15000 | 5000 | 14000 | 5600 | NS | 7480 | NS | 3300 | 15000 | 230 | NS | 240 | 12000 | 560 | 13000 E | 260 | 11000 E | 370 | 11000 E | 240 | 11000 E | 230
Zinc, Dissolved | 18000 | 680 | 19000 | 91 J- | 19000 | 46 | 20000 | 30 | 18000 | 260 | 18000 | 35 | NS | 11000 | 15000 | NA | 15000 | 230 | 14000 | 300 | NS | 218 | NS | 1400 J+ | 14000 | 110 J+ | NS | 130 | 11000 | 120 | 12000 E | 160 | 11000 E | 260 | 11000 E |  | 11000 E | 130
U | Indicates the analyte was analyzed for but not detected above the method detection limit, which is shown
J | The analyte was positively identified; the associated value is the approximate concentration of the analyte in the sample
E | Indicates the concentration of analyte exceeded the calibration range of laboratory analysis
+ | Result is estimated and may be biased high
- | Result is estimated and may be biased low
* | Sample from 12/1/2015 was collected during a 2 hour IWTP upset.
Notes: The flow rates are flows through the IWTP and not flows from the Gold King Mine adit.
Inlet sample location ID is GSTI. Outlet sample location is GSTO. Results for treatment plant discharges from 12/1, 12/8, 12/17, 12/23, and 1/5 are the weighted average of clarifier overflow (location ID GSTO-C) and filtrate (location ID GSTO-F) sample concentrations (C). Clarifier overflow and sludge flow (Q) measurements reported by Alexco at the times nearest sampling were averaged and used in the following equation: CGSTO = (COverflow*QOverflow + CFiltrate*QFiltrate) / (QOverflow+QFiltrate).
Samples taken on 4/12/2016 at a flow rate of 746 GPM were only analyzed for total metals and not dissolved metals. All other water treatment samples taken on 4/12/2016 were analyzed for both total and dissolved metals.
Filtrate recycle was installed on 1/19/2016 which eliminated filtrate effluent to Cement Creek. The GSTO flow is equal to the GSTO-C flow as of 1/19/2016 and GSTO-F effluent is no longer being considered for percent removal calculations. The location where the filtrate recycle entered the treatment system was changed on 2/3/2016 to improve particle flocculation.
Flow records begin 10/22/2015 at 20:22 so flow rates were not recorded for the 10/19/2015 sample and the flow rate on 10/22/2015 was estimated using the daily average flow. The 12/1/2015 sample did not have flow records during the IWTP upset and the flow rate was estimated based on the closest flow measurement to sample collection time. The flow rates on 4/12/2016 were the flow rates during sample collection time. All other sample events have estimated flow rates based on the three flow measurements taken closest to sample collection time.

## Percent Removal
Analyte | 2015-10-19 | 2015-10-22 | 2015-10-26 | 2015-10-29 | 2015-11-03 | 2015-11-05 | 2015-12-08 | 2015-12-17 | 2015-12-23 | 2016-01-05 | 2016-02-03 | 2016-02-04 | 2016-02-05 | 2016-02-18 | 2016-03-25 | 2016-04-12 | 2016-04-12 | 2016-04-12
|  | 481 GPM | 422 GPM | 404 GPM | 557 GPM | 570 GPM | 514 GPM | 571 GPM | 521 GPM | 487 GPM | 614 GPM | 671 GPM | 676 GPM | 508 GPM | 514 GPM | 638 GPM | 746 GPM | 961 GPM
Operating Parameters Reported by Alexco (Daily average except as noted)
Flow | NA | NA | 488 | 418 | 552 | 553 | 525 | 543 | 520 | 500 | 484 | 474 | 474 | 471 | 508 | 638* | 746* | 961*
pH at time of sampling | NA | 8.9# | 9.26 | 8.34 | 7.45 | 7.93 | 9.37 | 8.71 | 8.56 | 8.47 | 8.44 | 8.73 | 8.75 | 8.55 | 8.2 | 8.5* | 8.6* | 8.6*
Overflow Turbidity | NA | NA | NA | NA | NA | NA | 2 | 2.2 | 0.7 | 2 | 46.3 | 2.9 | 0.3 | 10.3 | 1.935* | 2.4* | 1.7* | 3.4*
Percent Removal in IWTP
Aluminum | 79.5% | 93.5% | 79% | 69% | 42.9% | 42.9% | 69.7% | 71.5% | 72.3% | 64.8% | 78.7% | 97.8% | 97.9% | 94.1% | 98.6% | 98.5% | 98.7% | 98.7%
Aluminum, Dissolved | 91.1% | 97% | 97.5% | 92.5% | 98.8% | 97.8% | NS | 98.4% | 96.9% | 98.2% | 86.3% | 97.5% | 97.6% | 99.2% | 98.2% | 97.9% |  | 97.7%
Arsenic | 96.4% | 98.7% | 91.5% | 86% | 60.7% | 70% | 79.2% | 73.8% | 70.2% | 74.2% | 82.6% | 98.4% | 98.4% | 95.2% | 98.2% | 97.8% | 97.8% | 97.8%
Arsenic, Dissolved | 66.4% | 82.4% | 85.8% | 98.4% | 75.3% | 76.9% | NS | 71.5% | 62.6% | 71.1% | 18.8% | 76.9% | 76.9% | 97.2% | 57% | 75.3% |  | 75.3%
Cadmium | 81.1% | 90.5% | 75% | 73.7% | 40% | 39.3% | 64.6% | 58.9% | 64.9% | 55.8% | 65.2% | 90.9% | 90.9% | 87.8% | 88.8% | 83.9% | 87.2% | 87.8%
Cadmium, Dissolved | 94.2% | 93.6% | 95.1% | 99.7% | 89.1% | 95.6% | NS | 90.6% | 91.1% | 90.8% | 78.3% | 92.2% | 91.7% | 91.1% | 89.5% | 85.4% |  | 88.9%
Copper | 84% | 96.3% | 80.5% | 75% | 40.9% | 44.4% | 64.8% | 65.5% | 70.2% | 57.1% | 79.1% | 99.2% | 99.1% | 95.8% | 99.2% | 99.1% | 99.3% | 99.2%
Copper, Dissolved | 96.1% | 99.7% | 100% | 99.9% | 99.4% | 100% | NS | 99.8% | 98.8% | 99.7% | 91.7% | 99.9% | 99.8% | 99.9% | 99.9% | 99.9% |  | 99.9%
Iron | 88.4% | 96.8% | 84.5% | 78.8% | 50.6% | 52.9% | 75.7% | 73.5% | 74% | 67.2% | 78.8% | 99.2% | 99.2% | 95.8% | 99.3% | 99.2% | 99.4% | 99.3%
Iron, Dissolved | 96.1% | 99.7% | 99.9% | 100% | 99.3% | 100% | NS | 99.9% | 98.8% | 99.9% | 90.4% | 99.8% | 99.8% | 100% | 100% | 100% |  | 99.9%
Lead | 89.1% | 97.5% | 87.2% | 79.7% | 34.5% | 63.3% | 79.5% | 75.7% | 71.7% | 74% | 82.3% | 99.1% | 99.3% | 93.2% | 99.3% | 99.1% | 99.7% | 99.7%
Lead, Dissolved | 91.4% | 98.4% | 99.6% | 99.8% | 98.3% | 99.2% | NS | 97.7% | 91.1% | 97.8% | 0% | 96% | 94.8% | 98.9% | 92.2% | 91.8% |  | 77.5%
Manganese | 57.1% | 60.7% | 40.7% | 74.1% | 10.3% | 23.3% | 49.2% | 27.3% | 24.7% | 19.4% | 20.8% | 37.5% | 37.5% | 36.4% | 30.4% | 30% | 30% | 35%
Manganese, Dissolved | 64.6% | 58.6% | 53.6% | 99.9% | 33.3% | 55.2% | NS | 32.4% | 41.3% | 36.1% | 17.4% | 34.8% | 39.1% | 38.1% | 27.3% | 30% |  | 35%
Zinc | 83.9% | 96.1% | 79.4% | 76.5% | 45% | 44.4% | 66.3% | 67% | 59.9% | 46.5% | 78% | 98.5% | 98.4% | 95.3% | 98% | 96.6% | 97.8% | 97.9%
Zinc, Dissolved | 96.2% | 99.5% | 99.8% | 99.9% | 98.6% | 99.8% | NS | 98.5% | 97.8% | 98.4% | 90% | 99.2% | 99.1% | 98.9% | 98.7% | 97.6% |  | 98.8%
* | Measurements taken at time of sampling or average of measurements directly before and after time of sampling
# | Operating pH as reported by Alexco at 20:54, the closest IWTP measurement available
NS | Not sampled
Notes: Filtrate recycle was installed on 1/19/2016 which eliminated filtrate effluent to Cement Creek. The GSTO flow is equal to the GSTO-C flow as of 1/19/2016 and GSTO-F effluent is no longer being considered for percent removal calculations.
Percent Removal = (CIn – COut)/CIn. Percent removal was calculated using the method detection limit for non-detects, resulting in an artificially low percent removal. This primarily affected the arsenic percent removal.
Sample collected on 12/01/2015 was representative of upset conditions and the percent removal is not shown.
Inlet sample location ID is GSTI. Outlet sample location is GSTO. Results for treatment plant discharges from 12/1, 12/8, 12/17, 12/23, and 1/5 are the weighted average of clarifier overflow (location ID GSTO-C) and filtrate (location ID GSTO-F) sample concentrations (C). Clarifier overflow and sludge flow (Q) measurements reported by Alexco at the times nearest sampling were averaged and used in the following equation: CGSTO = (COverflow*QOverflow + CFiltrate*QFiltrate) / (QOverflow+QFiltrate).
Samples taken on 4/12/2016 at a flow rate of 746 GPM were only analyzed for total metals and not dissolved metals. All other water treatment samples taken on 4/12/2016 were analyzed for both total and dissolved metals.
Manganese removal requires a higher pH set point that would generate additional precipitation solids. Manganese concentrations measured upstream of the IWTP (sample location CC18) during non-runoff (August-April) sampling events from 2009-2014 were: average dissolved manganese 18,800 µg/L, maximum dissolved manganese 24,300 µg/L, average total manganese 18,900 µg/L, maximum total manganese 24,200 µg/L.