## Pre-Adsil
ARI Conditions
[10 empty] | 85 | 95 | 105 | 115 | 125
FIGURE H-1 HVAC Data Sheet and EER Calculation
Manufacturer: |  | Brand X |  |  | Published EER: | 10.2 | Btu/W-hr | (CU Only)
Model Number: |  | Big Guy 60 |  |  | Calculated EER: | 10.8414 | Btu/W-hr | (CU Only)
Serial Number |  | 123456 |  |  | Nominal Capacity: | 5 | tons
Equipment Type: |  | Split-System |  |  | Age | 5 | years
Year Manufactured: |  | 1999 |  |  | Coil Conditon | 12.3% | (% degraded)
Location |  | ACME Warehouse |  |  | Present Condition EER | 9.5688 | Btu/W-hr
Tag |  | SS-2 |  |  | kW/ton | 1.2541
Compressor Data
Running load Amps: |  | 18 | Amps |  | Power supply: | 3-phase
Nameplate Voltage: |  | 208 | Volts |  | Phase adjustment: | 1.73 | (=1.0 if single phase)
Power factor: |  | 0.8 |  |  | Compressor quantity: | 1
Condensing Fan Data
Full load Amps: |  | 1.4 | Amps |  | Power supply: | 3-phase
Nameplate Voltage: |  | 208 | Volts |  | Phase adjustment: | 1.73 | (=1.0 if single phase)
Adjust FLA to RLA: |  | 0.7 |  |  | Fan quantity: | 1
Evaporator fan data (if applicable)
Full load Amps: |  | NA | Amps |  | Power supply: | 1 or 3-phase
Nameplate Voltage: |  | NA | Volts |  | Phase adjustment: | 1 or 1.73
Adjust FLA to RLA: |  | 0.7 |  |  | Fan quantity: | NA
Calculated compressor load: |  |  |  | 5.1817 | kW
Calculated condensing fan load: |  |  |  | 0.35264 | kW
Calculated evaporator fan load |  |  |  | #VALUE! | kW
Total calculated load for equipment: |  |  |  | 5.5343 | kW - Condensing side only
Assumptions
Condenser Coil Assessment |  |  | 12.3% | Performance Degradation
Age of Unit
| New |  | 0 | 0 | Put a "1" in the appropriate cell to
| 2-9 years |  | 15 | 0 | correspond with the age of the unit.
| 10-14 years |  | 20 | 0
| 15 or more | 1 | 25 | 25 |  |  |  |  | kVa
Coil Cleanliness |  |  |  | 0
| Coated |  | 25 | 0 | Put a "1" if unit is currently coated
| Clean | 0.7 | 0 | 0 | Place a percentage (.01-1) to represent
| Dirty | 0.2 | 75 | 15 | percentage of the fins that are considered
| Clogged | 0.1 | 100 | 10 | to be clean, dirty, clogged, or plugged. These
| Plugged |  | 125 | 0 | must sum to 100% |  |  |  | kva
Fin Condition |  |  |  | 0 |  |  |  |  | 1.58
| Like New | 0.1 | 0 | 0 | Percentage in "like new" condition
| Some Bent | 0.05 | 50 | 2.5 | Percentage "bent"
| Smashed |  | 75 | 0 | Percentage "smashed"
| Dull/rough | 0.9 | 10 | 9 | Percentage "dull/rough, corroded, pitted,
| Corroded |  | 25 | 0 | & flaking" plus percentage "like new",
| Pitted |  | 50 | 0 | must equal 100%.
| Flaking |  | 100 | 0
Fin-Tube Attachment |  |  |  | 0
| Like New | 1 | 0 | 0 | Place a"1" in the appropriate cell
| Corrosion |  | 10 | 0
| Some Loose |  | 25 | 0
| Many Loose |  | 50 | 0
Tubes |  |  |  | 0
| Clean Cu | 1 | 0 | 0 | Place a"1" in the appropriate cell
| Corrosion |  | 5 | 0
| Pitting |  | 10 | 0
| Leaks |  | 200 | 0
Mark "x" for all that apply. New is for equipment less than 6 months installed, that is not in Fair or Poor condition only. Clogged is for heavy accumulation of dirt or debris that does not completely block air flow. Condenser split is the temperature difference between the condensing temperature and the ambient or condenser inlet air. Based on indications that refrigerant charge and airflow is correct, and that the evaporator condition is good, a relatively low condenser split and subcool temperature is an indication of good condenser performance. The condenser does not have to elevate its temperature to reject the heat load if there is sufficient airflow and the coil and fin surfaces are clean and in good condition. Conversely, a fouled and damaged condenser coil must have a temperature that is much higher than ambient to reject the heat absorbed in the evaporator coil and in the compressor. A higher condensing temperature raises the discharge pressure of the compressor, thereby reducing system energy efficiency. A comparison of the condenser and liquid line temperature with the ambient temperature is a direct indication of condenser performance.